## Slide 1: Cooling Issues January 2022 - detector closing
Oleg Solovianov
Ludovico Pontecorvo
Stanislav Nemecek
Antonio Cervello Duato
Merve Nazlim Agaras
Dawit Mesfin Belayneh
Katherine Rees Hughes
Filipe Manuel Pedro Martins
Irakli Minashvili

## Slide 2
Maintenance of cooling station + EBC closer
11-12 January
EBC opening
13 January
Conflict with diffusion pump cables
EBC closed
24th January
LBC33, LBC49, EBC48 and EBC49 fixation. 19-23 Jan
LBC60 isolation valve rubber hose connection damaged by metallic PIN (on the EBC)
24th January
PPV Cycle (min)
January-February 2022

## Slide 3
Rubber hose
Metallic PIN

## Slide 4
EBC49
EBC48
LBC49
LBC33
LBC60

## Slide 5
MB-Side
HV-Side
IN
OUT
Internal Cooling of Tile Supper Drawer

## Slide 6
Cooling leak (EBA04) 2009
Metallic pipe corrosion

## Slide 7: Some special cases (LBA 56) 2012
The water leak problem was in the internal drawer but was impossible to precisely located it.
After several days, SD was inserted but ¼ of the SD has no water flow (a bypass was installed preventing the water to flow in the internal drawer – MB side)
Air bubbles
No increase in temperature is seen in DCS.
The PPV cycle of the cooling loop increased from 250 min to 350 min.
PPV: Elapsed time between vacuum pump cycles.

## Slide 8
 | Module | Date | From cooling disconnected | Impact in PPV cycle | 
1 | LBA56 | Jan. 2012 | MB internal | 100min (250🡪350min) | 
2 | EBA51 | March 2020 | ½ HV External | 30min | 
3 | LBC14 | April 2021 | MB external + HV internal | 100min | 
4 | LBC64 | Dec. 2021 | MB Internal + HV Internal | 50min | 
5 | LBC01 | Dec. 2021 | MB internal | 50min | 
6 | LBC33 | Jan. 2022 | HV side (internal + external) | 100min | 
7 | LBC49 | Jan. 2022 | HV side (internal + external) | 100min | 
8 | EBC48 | Jan. 2022 | HV side (internal + external) | 100min | 
9 | EBC49 | Jan. 2022 | HV side (internal + external) | 100min | 

## Slide 9
MB-Side
HV-Side
IN
OUT
Internal Cooling of Tile Supper: Drawer HV side excluded